Drinking Water Arsenic Filter

# Arsenic Removal Media

Description

Arsenil is a natural zeolite based media, which has been specially coated with Mn-substituted nanophase iron oxides (US Patent No. 6,790,363 B2).  The sample has excellent particle integrity and nanophase coated iron oxide does not get separated from zeolite during either treatment or backwashing.  Therefore, clogging of the filter is not anticipated.  This technology was developed by Dr. Rajan K. Vempati of ChK Group, Inc., who is an expert in nanophase-Fe oxide chemistry and mineralogy.  The Arsenil™ media will remove both Arsenic (III) and Arsenic (V) species from contaminated water without the need for external oxidation methods.

Specifications

- COLOR……………………………………….Reddish Brown

- DENSITY.……………………………………137 Lb/Cu.Ft.

- EFFECTIVE SIZE. …………………………..0.2 mm to 0.4 mm

- FE CONTENT                                                  Ranges from 9% to 10%

- SCREEN GRADING.………………………..40 to 80 mesh size

- SPECIFIC GRAVITY.……………………….2.2 g/cc

- SHIPPING WEIGHT.………………………..137 Lb/Cu.Ft.

Operational Parameters

- EBCT (typical range).………………..5 minutes or Less

- pH (operating range)…………………4.0 to 8.5

- TEMPERATURE (optimal)………….65 Deg F

- TCLP Results……………………..….Pass

Shipping containers                            Manufacturing Locations

1 U.S. Ton Supersacs                                             Detroit, Michigan

Arsenil - How it Can Help You Comply with the New Arsenic Rule

Arseni media can help municipal facilities comply with the EPA’s new Arsenic Rule.  By using this sturdy, high surface area media in your raw water treatment process you can efficiently adsorb arsenic and several other heavy metals in one easy step with little or no backwashing.  This media stands up to handling unlike any other existing technology on the market today.  Arsenil was designed to cope with the complex chemistries of As-containing water. Arsenil is not significantly affected by the presence of silica.  Once the media is exhausted it is simply replaced.  The expended media can be discarded in landfills and classified as non-hazardous waste based on TCLP tests.

Arsenil - Typical Results using a Single Column :

Arsenic Concentration	Si Level	EBCT†		Breakthrough‡

(ppb)	ppm	(min)	Bed Volume

110	2	10	5,200

18 	2	3	92,099

25 	2	5	51,124

25	25	10	22,597

25	50	20	10,629

† EBCT= Empty bed contact time

‡ Column breakthrough is defined when concentration of the effluent water is > 10 ppb